## Sheet1
Modbus TCP Communication Protocol Description
TCP Port |  |  | Modbus TCP
<!-- Physical Layer Setup: RS485, 1 start bit, 8 data bits, no bit for parity, 1 stop bit. --> <!-- TCP Port: 502 --> <!-- Link Layer Setup: Only RTU Mode Supported. --> <!-- Frame Length Uplimit: 256 Bytes. --> <!-- Register 1 is addressed as 0. --> <!-- PCS applicable version: R3.0 GFL -->
Classgrp_name & Functioncode | Address | Type | Item | 描述 | Description | Rang | Rate | Unit
classgrp_name="Trip_Element" FunctionCode:02H Read only | 1 |  | Pre_Alm | 整租启动 | Preliminary Alarm Signal | 1：enable 0：disable
| 2 |  | Op_Overall | 保护动作 | General Protection Operate Signal | 1：enable 0：disable
| 3 |  | 76.Op | 直流过流保护 | DC Overcurrent Protection | 1：enable 0：disable
| 4 |  | 59DC.Op | 直流过压保护动作 | DC Overvoltage Protection | 1：enable 0：disable
| 5 |  | 27DC.Op | 直流欠压保护动作 | DC Undervoltage Protection | 1：enable 0：disable
| 6 |  | RevDC-Polar.Op | 直流反接保护动作 | Reverse Connection Protection | 1：enable 0：disable
| 7 |  | 51P.Op | 交流过流保护动作 | AC Overcurrent Protection | 1：enable 0：disable
| 8 |  | 50Q.Op | 负序电流动作 | AC Current Unbalance Protection | 1：enable 0：disable
| 9 |  | 59P.Op | 交流过压保护动作 | AC Overvoltage Protection | 1：enable 0：disable
| 10 |  | 27P.Op | 交流欠压保护动作 | AC Undervoltage Protection | 1：enable 0：disable
| 11 |  | 59Q.Op | 负序电压动作 | AC Voltage Unbalance Protection | 1：enable 0：disable
| 12 |  | 81O.Op | 过频保护动作 | AC Overfrequency Protection | 1：enable 0：disable
| 13 |  | 81U.Op | 欠频保护动作 | AC Underfrequency Protection | 1：enable 0：disable
| 14 |  | 26.Op | 过温保护动作 | Over Temperature Protection | 1：enable 0：disable
| 15 |  | LowTemp.Op | 低温闭锁动作 | Low Temperature Protection | 1：enable 0：disable
| 16 |  | OvLd.Op | 过载保护动作 | Over Load Protection | 1：enable 0：disable
| 17 |  | LVRT-Prot.Op | LVRT保护动作 | Low Voltage Ride Through Protection | 1：enable 0：disable
| 18 |  | LVRT_SWITCH |  | Low Voltage Ride Through Switch | 1：enable 0：disable
| 19 |  | Op_Drive | 驱动保护动作 | Driving Protection | 1：enable 0：disable
| 20 |  | Op_Drive_A | A相驱动保护动作 | Driving Protection_Phase A | 1：enable 0：disable
| 21 |  | Op_Drive_B | B相驱动保护动作 | Driving Protection_Phase B | 1：enable 0：disable
| 22 |  | Op_Drive_C | C相驱动保护动作 | Driving Protection_Phase C | 1：enable 0：disable
| 23 |  | VTS.Op | PT异常保护动作 | Voltage Transformer Supervision Protection | 1：enable 0：disable
| 24 |  | LeakCurrProt.Op |  | Leakage Current Protection Operate | 1：enable 0：disable
| 25 |  | NP_VoltUnbal_PRT |  | Neutral Point Voltage Unbalance Protection | 1：enable 0：disable
| 26 |  | 51PC.Op | 谐波保护动作 | Capacitor overcurrent protection | 1：enable 0：disable
| 27 |  | PulseSynErrProt.Op | 同步脉冲异常保护动作 | Pulse Syn. Error Protection | 1：enable 0：disable
| 28 |  | Alm_InternalFault_Conv | 变流器内部故障 | Alarm_Internal Fault_Converter | 1：enable 0：disable
| 29 |  | FAULT_IC |  | Fault_Internal Circuit | 1：enable 0：disable
| 30 |  | PRT_Fan |  | Protection_Fan Fault | 1：enable 0：disable
| 31 |  | BI_trigger_DFR |  | Trigger Digital Fault Record_Binary Input | 1：enable 0：disable
| 32 |  | telectrl_wave_triger |  | Trigger Digital Fault Record_Remote | 1：enable 0：disable
| 33 |  | rec_manual_trig_flag |  | Trigger Digital Fault Record_Manual | 1：enable 0：disable
| 34 |  | CLOSE_INV_LB |  | Trigger Digital Fault Record_AC-Contactor Closed | 1：enable 0：disable
| 35 |  | PROTECT_LB |  | Trigger Digital Fault Record_General Protection Operate | 1：enable 0：disable
| 36 |  | FVRT_TRIG |  | Frequency Voltage Ride Through Trigger | 1：enable 0：disable
| 37 |  | Wave_Trig_Hold |  | Trigger Digital Fault Record Hold | 1：enable 0：disable
| 38 |  | Sig_Conv_Stopped_BMS |  | PCS is stopped by BMS | 1：enable 0：disable
| 39 |  | Alm_Comm_BMS |  | Alarm_BMS Communication Failure | 1：enable 0：disable
| 40 |  | BI_Fuse_OK |  | Fuse OK | 1：enable 0：disable
| 41 |  | Alm_ModeChk |  | Alarm_Mode Check Error | 1：enable 0：disable
| 42 |  | Alm_Comm_SCADA |  | Alarm_EMS Communication Failure | 1：enable 0：disable
| 43 |  | Mul_Protections |  | Frequent faults occurred in a short period of time. | 1：enable 0：disable
| 44 |  | LVRT_HAPPEN |  | Low Voltage Ride Through Happened | 1：enable 0：disable
| 45 |  | Op_Overall_SL |  | Overall Operation Signal_Link | 1：enable 0：disable
| 46 |  | START_FAIL |  | Startup Failure Alarm | 1：enable 0：disable
| 47 |  | Alm_Comm_MASL |  | Master Link Communication Alarm | 1：enable 0：disable
| 48 |  | TRIP_BLOCK.Op |  | Trip Block Operate | 1：enable 0：disable
| 49 |  | Devicebs_Boardstall |  | Device Bus Board Stall | 1：enable 0：disable
| 50 |  | BH6 |  | spare | 1：enable 0：disable
| 51 |  | BH7 |  | spare | 1：enable 0：disable
classgrp_name="Self-check_Alarm" FunctionCode:02H Read only | 3001 |  | Alm_Device | 装置报警 | Alarm_Device | 1：enable 0：disable
| 3002 |  | Fail_Device | 装置闭锁 | Failure_Device | 1：enable 0：disable
| 3003 |  | Alm_Settings_MON | 定值校验出错 | Alarm_Settings_Verification Error | 1：enable 0：disable
| 3004 |  | Fail_SettingItem_Chgd | 定值项变化告警 | Failure_Setting Items Changed | 1：enable 0：disable
| 3005 |  | Fail_Setting_OvRange | 定值超范围 | Failure_Settings_Out of Range | 1：enable 0：disable
| 3006 |  | Fail_BoardConfig | 板卡配置错误 | Failure_Board Configuration Error | 1：enable 0：disable
| 3007 |  | Alm_Sample | 采样异常 | Alarm_Sampling Error | 1：enable 0：disable
| 3008 |  | Alm_TimeSyn | 对时异常 | Alarm_Time Syn. Error | 1：enable 0：disable
| 3009 |  | Alm_Version | 版本错误报警 | Alarm_Version Error | 1：enable 0：disable
| 3010 |  | Alm_CommTest | 通信传动报警 | Alarm_Communication Test | 1：enable 0：disable
| 3011 |  | Alm_BOTest | 出口传动测试报警 | Alarm_Binary Output Test | 1：enable 0：disable
| 3012 |  | Alm_OptoDC | 光耦电源异常 | Alarm_Optocoupler Power Error | 1：enable 0：disable
| 3013 |  | Alm_Board11 |  | Alarm_Board 11 Fault | 1：enable 0：disable
| 3014 |  | Alm_Board12 |  | Alarm_Board 12 Fault | 1：enable 0：disable
| 3015 |  | Alm_Board14 |  | Alarm_Board 14 Fault | 1：enable 0：disable
classgrp_name="Binary_Input" FunctionCode:02H Read only | 6001 |  | Link_RmtRegu | 后台控制使能 | Logic Link_Enable the PCS power command controlled by HMI | 1：enable 0：disable
| 6002 |  | Link_BMS_Ctrl | BMS控制使能 | Logic Link_Enable the PCS power command controlled by BMS | 1：enable 0：disable
| 6003 |  | Link_CCU_Ctrl | CCU控制使能 | Logic Link_Enable the PCS power command controlled by CCU(Central Control Unit or called PMS-Power Management System, there is no such device in this project) | 1：enable 0：disable
| 6004 |  | Link_Start_Conv | 启动命令 | Logic Link_Converter Starting | 1：enable 0：disable
| 6005 |  | Link_Stop_Conv | 停机命令 | Logic Link_Converter Stopping | 1：enable 0：disable
| 6006 |  | Link_Standby_Conv | 待机命令 | Logic Link_Converter on Standby | 1：enable 0：disable
| 6007 |  | Link_U_DC_Ctrl |  | Logic Link_Enable DC Voltage Control Mode | 1：enable 0：disable
| 6008 |  | Link_P_AC_Ctrl |  | Logic Link_Enable AC Power Control Mode | 1：enable 0：disable
| 6009 |  | Link_PF_Ctrl |  | Logic Link_Enable Power Factor Control Mode | 1：enable 0：disable
| 6010 |  | Link_Island_Ctrl |  | Logic Link_Enable Islanding Control Mode | 1：enable 0：disable
| 6011 |  | Link_VF_Ctrl |  | Logic Link_Enable VF Control Mode | 1：enable 0：disable
| 6012 |  | Link_U2_Ctrl |  | Logic Link_Enable Negative Voltage Control Mode | 1：enable 0：disable
| 6013 |  | Link_End_To_ConstU_DC_Ctrl |  | Logic Link_Enable Automatic Switching into Constant DC Voltage Mode (at the end of charging or discharging) | 1：enable 0：disable
| 6014 |  | Link_BatPrecharge |  | Logic Link_Enable Battery Precharging Function | 1：enable 0：disable
| 6015 |  | Link_ZeroP_To_Standby | 投零功率运行自动转待机 | Logic Link_Enable the Function "when both of the active and reactive power commands are zero, the PCS switches into Standby mode automatically". | 1：enable 0：disable
| 6016 |  | Link_LVRT_Ctrl | 投LVRT控制 | Logic Link_Enable Low Voltage Ride Through Control Mode | 1：enable 0：disable
| 6017 |  | Link_SOC_To_Standby |  | Logic Link_Enable the Function "when SOC rises to a certain value at the end of charging, the PCS switches into Standby mode automatically. When SOC falls to a certain value at the end of discharging, the PCS switches into Standby mode automatically". | 1：enable 0：disable
| 6018 |  | Link_DeblkPWM_Standby |  | Logic Link_Enable the Function "After a certain time of switching to standby mode, try to Deblock PCS" | 1：enable 0：disable
| 6019 |  | Link_Island_LimitP |  | Logic Link_Enable Power Limitation Function (no more than maximum PCS output power) in off-grid mode | 1：enable 0：disable
| 6020 |  | Link_Watchdog_SCADA |  | Logic Link_Enable SCADA Watchdog Function | 1：enable 0：disable
| 6021 |  | 51P/76.Link | 投过流保护 | Logic Link_Enable Overcurrent Protection | 1：enable 0：disable
| 6022 |  | 81.Link | 投过欠频保护 | Logic Link_Enable AC Overfrequency/Underfrequency Protection | 1：enable 0：disable
| 6023 |  | 81.Link_AutoChgP | 投过欠频自动改变功率 | Logic Link_Enable AC Overfrequency/Underfrequency AutoChange Protection | 1：enable 0：disable
| 6024 |  | 27/59.Link | 投交流过欠压保护 | Logic Link_Enable AC Overvoltage/Undervoltage Protection | 1：enable 0：disable
| 6025 |  | OvLd.Link | 投变流器过载保护 | Logic Link_Enable Converter Overload Protection | 1：enable 0：disable
| 6026 |  | 59DC.Link | 投直流过压保护 | Logic Link_Enable DC Overvoltage Protection | 1：enable 0：disable
| 6027 |  | 27DC.Link | 投直流欠压保护 | Logic Link_Enable DC Undervoltage Protection | 1：enable 0：disable
| 6028 |  | 27DC.Link_Trp_DC-CB | 投直流欠压保护跳断路器 | Logic Link_Enable DC Undervoltage Protection to Trip DC CB | 1：enable 0：disable
| 6029 |  | 51Q/59Q.Link | 投变流器负序保护 | Logic Link_Enable Coverter Negative-Sequence Protection | 1：enable 0：disable
| 6030 |  | 26.Link | 投模组过温保护 | Logic Link_Enable Submodule Over Temperature Protection | 1：enable 0：disable
| 6031 |  | RevDC-Polar.Link | 投直流反接保护 | Logic Link_Enable DC Reverse Connection Protection | 1：enable 0：disable
| 6032 |  | Link_VTS | 投PT异常保护 | Logic Link_Enable Voltage Transformer Supervision Protection | 1：enable 0：disable
| 6033 |  | SynPulseProt.Link | 投载波不同步保护 | Logic Link_Enable Pulse Syn. Error Protection | 1：enable 0：disable
| 6034 |  | Sig_P_AC_Ctrl | 交流功率控制模式 | Signal_AC Power Control Mode | 1：enable 0：disable
| 6035 |  | Sig_Island_Ctrl |  | Signal_Islanding Mode | 1：enable 0：disable
| 6036 |  | Sig_VF_Ctrl |  | Signal_VF Control Mode | 1：enable 0：disable
| 6037 |  | Sig_I_DC_Ctrl | 直流电流控制模式 | Signal_DC Current Control Mode | 1：enable 0：disable
| 6038 |  | Sig_P_DC_Ctrl | 直流功率控制模式 | Signal_DC Power Control Mode | 1：enable 0：disable
| 6039 |  | Sig_U_DC_Ctrl | 直流电压控制模式 | Signal_DC Voltage Control Mode | 1：enable 0：disable
| 6040 |  | Sig_PF_Ctrl | 功率因数控制模式 | Signal_Power Factor Control Mode | 1：enable 0：disable
| 6041 |  | Sig_Ready_Conv | 变流器就绪 | Signal_Converter is Ready | 1：enable 0：disable
| 6042 |  | Sig_Ready_Grid-Conn_Conv | 并网条件具备 | Signal_Grid Connection condition is satisfied | 1：enable 0：disable
| 6043 |  | Sig_Ready_BlackStart_Conv | 黑启动条件具备 | Signal_Black Start condition is satisfied | 1：enable 0：disable
| 6044 |  | Sig_Ready_OneKeyStart_Conv | 一键启动条件具备 | Signal_One-Key Start condition is satisfied | 1：enable 0：disable
| 6045 |  | Sig_PWM_Blkd_Conv | 脉冲闭锁 | Signal_Pulse Blocked the Converter | 1：enable 0：disable
| 6046 |  | Sig_Opr_Conv | 运行状态 | Signal_Converter Operation Condition | 1：enable 0：disable
| 6047 |  | Sig_Standby_Conv | 待机状态 | Signal_Converter Standby Condition | 1：enable 0：disable
| 6048 |  | Sig_Stop_Conv | 停机状态 | Signal_Converter Stop Condition | 1：enable 0：disable
| 6049 |  | Sig_Opr_Stdby_Conv | 运行或待机 | Signal_Converter Operation or Standby Condition | 1：enable 0：disable
| 6050 |  | Sig_Opr_OK_Conv | 正常运行 | Signal_Converter in Good Operation Condition | 1：enable 0：disable
| 6051 |  | Sig_Opr_Alm_Conv | 告警运行 | Signal_Converter in Alarm Operation Condition | 1：enable 0：disable
| 6052 |  | Sig_Stop_Normal_Conv | 正常停机 | Signal_Converter Normal Stop | 1：enable 0：disable
| 6053 |  | Sig_Stop_Fault_Conv | 故障停机 | Signal_Converter Faulty Stop | 1：enable 0：disable
| 6054 |  | Sig_Stop_Chrgd_Conv | 充满自动停机 | Signal_Converter stops after being fully charged | 1：enable 0：disable
| 6055 |  | Sig_Stop_DisChrgd_Conv | 放空自动停机 | Signal_Converter stops after being fully discharged | 1：enable 0：disable
| 6056 |  | Sig_NearlyChrgd_Conv | 充电末期状态 | Signal_Converter is almost fully charged | 1：enable 0：disable
| 6057 |  | Sig_NearlyDisChrgd_Conv | 放电末期状态 | Signal_Converter is almost fully discharged | 1：enable 0：disable
| 6058 |  | Sig_Charging_Conv | 电池充电状态 | Signal_Converter Charging Status | 1：enable 0：disable
| 6059 |  | Sig_Discharging_Conv | 电池放电状态 | Signal_Converter Disharging Status | 1：enable 0：disable
| 6060 |  | Sig_RequestPrecharge | 预充电请求 | Signal_Request Pre-charging | 1：enable 0：disable
| 6061 |  | LVRT_SWITCH | LVRT功能切换成功 | Signal_Low Voltage Ride Through Function Swichover Successfully | 1：enable 0：disable
| 6062 |  | Alm_Conv | 变流器告警 | Alarm_General Alarm of Converter | 1：enable 0：disable
| 6063 |  | Alm_ModeChk | 模式校验错误 | Alarm_Mode Check Error | 1：enable 0：disable
| 6064 |  | 26.Alm | 高温告警 | Alarm_Over Temperature | 1：enable 0：disable
| 6065 |  | Alm_Decr_P_Output_OvTemp | 高温降额 | Alarm_Decrease Output Power Due to Over Temperature | 1：enable 0：disable
| 6066 |  | Alm_ThermometerFail | 模组测温元件异常 | Alarm_Thermometer Failure | 1：enable 0：disable
| 6067 |  | Alarm_Fan | 风机回路异常 | Alarm_Fan Circuit | 1：enable 0：disable
| 6068 |  | Alm_DC-SideInsulFail | 直流绝缘异常 | Alarm_DC Side Insulation Failure | 1：enable 0：disable
| 6069 |  | Alm_InsulDetectorFail | 绝缘监测失效 | Alarm_Insulation Detector Failure | 1：enable 0：disable
| 6070 |  | Sig_AC-ContactorFail |  | Alarm_AC-Contactor Operation Failure | 1：enable 0：disable
| 6071 |  | AC-Contactor_Fault_Conv |  | Alarm_AC-Contactor Position Lost | 1：enable 0：disable
| 6072 |  | Sig_DC-Chrg_TimeOut | 直流开关预充电超时 | Signal_DC Busbar Charging Time Out | 1：enable 0：disable
| 6073 |  | DC_BREAK_TJ |  | DC Breaker Trip/Close Status | 1：enable 0：disable
| 6074 |  | Alm_U_DC |  | DC Voltafe Sampling error | 1：enable 0：disable
| 6075 |  | BI_Start_Conv | 开机旋钮位状态 | Binary Input_Start Converter | 1：enable 0：disable
| 6076 |  | BI_Stop_Conv | 关机旋钮位状态 | Binary Input_Stop Converter | 1：enable 0：disable
| 6077 |  | BI_EmergStop_Conv | 紧急停机旋钮状态 | Binary Input_Emergency Shut-down Converter | 1：enable 0：disable
| 6078 |  | BI_All_EmergStop_Disable |  | Binary Input_All_EmergStop_Disable | 1：enable 0：disable
| 6079 |  | BI_Fuse_OK |  | Binary Input_Fuse OK | 1：enable 0：disable
| 6080 |  | BI_Manual_Close | 手动分闸 | Binary Input_Manual Close | 1：enable 0：disable
| 6081 |  | BI_Manual_Open | 交流开关合位 | Binary Input_Manual Open | 1：enable 0：disable
| 6082 |  | BI_AC-Contactor | 直流断路器位置 | Binary Input_AC Contactor status | 1：enable 0：disable
| 6083 |  | BI_DC-CB | 直流绝缘异常开入 | Binary Input_DC CB status | 1：enable 0：disable
| 6084 |  | BI_DC-SideInsul_Alm | 放电接触器位置 | Binary Input_DC Side Insulation Error | 1：enable 0：disable
| 6085 |  | BI_DisChrgContactor | 散热风机启动 | Binary Input_Discharge Contactor status | 1：enable 0：disable
| 6086 |  | BI_Start_Fan | 直流负极充电接触器位置 | Binary Input_Fan Start | 1：enable 0：disable
| 6087 |  | BI_DC-ChrgContactor2 | 直流正极充电接触器位置 | Binary Input_DC Charging Contactor 2 Position | 1：enable 0：disable
| 6088 |  | BI_DC-ChrgContactor | 交流防雷器空开位置 | Binary Input_DC Charging Contactor 1 Position | 1：enable 0：disable
| 6089 |  | BI_Clsd_MCB_AC-SPD | 交流防雷器异常 | Binary Input_MCB Position of AC Surge Protective Device | 1：enable 0：disable
| 6090 |  | BI_AC-SPD_Alm | 直流防雷器异常 | Binary Input_AC Surge Protective Device Error | 1：enable 0：disable
| 6091 |  | BI_DC-SPD_Alm | 电抗器温度正常 | Binary Input_DC Surge Protective Device Error | 1：enable 0：disable
| 6092 |  | BI_ReactorTemp_OK |  | Binary Input_Reactor Temperature is normal | 1：enable 0：disable
| 6093 |  | BI_AC-ChrgContactor |  | Binary Input_AC Charging Contactor Position | 1：enable 0：disable
| 6094 |  | BI_AC-Contactor(NC) | 散热风机正常 | Binary Input_AC Contactor in Open Position | 1：enable 0：disable
| 6095 |  | COOLFAN_OK |  | Binary Input_Cool fan is ok | 1：enable 0：disable
| 6096 |  | BI_ExtEmergStop_Disable |  | Binary Input_External Emergency Stop_Disable | 1：enable 0：disable
| 6097 |  | YK_Start | 后台下发停机命令 | Remote Control_Start Command | 1：enable 0：disable
| 6098 |  | YK_Stop | 后台下发待机合命令 | Remote Control_Stop Command | 1：enable 0：disable
| 6099 |  | YK_Standby_Close | 后台下发待机分命令 | Remote Control_Standby Close Command | 1：enable 0：disable
| 6100 |  | YK_Standby_Open |  | Remote Control_Standby Open Command | 1：enable 0：disable
| 6101 |  | YK_OneKeyStart |  | Remote Control_One Key Start Command | 1：enable 0：disable
| 6102 |  | YK_Open_DCCB | 后台分直流断路器 | Remote Control_DC CB Open Command | 1：enable 0：disable
| 6103 |  | YK_Close_DCCB | CCU下发启动命令 | Remote Control_DC CB Close Command | 1：enable 0：disable
| 6104 |  | Cmd_StartConv_CCU | CCU下发停机命令 | Command_Start Converter by CCU(or called PMS) | 1：enable 0：disable
| 6105 |  | Cmd_StopConv_CCU | CCU下发交流功率控制模式 | Command_Stop Converter by PMS | 1：enable 0：disable
| 6106 |  | Cmd_P_AC_Ctrl_CCU |  | Command_AC Power Control Mode by PMS | 1：enable 0：disable
| 6107 |  | Cmd_Island_Ctrl_CCU | 电池正常 | Command_Island Control Mode by PMS | 1：enable 0：disable
| 6108 |  | Sig_Bat_OK | 电池充满 | Signal_BMS Operation Condition is OK | 1：enable 0：disable
| 6109 |  | Sig_Bat_FullyChrgd | 电池放空 | Signal_BMS Fully Charged | 1：enable 0：disable
| 6110 |  | Sig_Bat_FullyDisChrgd | 电池告警 | Signal_BMS Fully Discharged | 1：enable 0：disable
| 6111 |  | Sig_Bat_Alm | BMS下发待机命令 | Signal_BMS Alarm | 1：enable 0：disable
| 6112 |  | Cmd_Bat_Standby | BMS下发停机命令 | Command_Standby Command by BMS | 1：enable 0：disable
| 6113 |  | Cmd_Bat_Stop | BMS下发紧急停机命令 | Command_Stop Command by BMS | 1：enable 0：disable
| 6114 |  | Cmd_Bat_Emgcy_Stop | PWM脉冲被BMS闭锁 | Command_Emergency Stop Command by BMS | 1：enable 0：disable
| 6115 |  | Sig_PWM_Blkd_BMS | BMS通讯故障 | Signal_BMS block PWM Pulses | 1：enable 0：disable
| 6116 |  | Alm_Comm_BMS | CCU通讯故障 | Alarm_BMS Communication Failure | 1：enable 0：disable
| 6117 |  | Alm_Comm_CCU |  | Alarm_PMS Communication Failure | 1：enable 0：disable
| 6118 |  | Alm_Comm_SCADA |  | Alarm_EMS Communication Failure | 1：enable 0：disable
| 6119 |  | Op_Overall |  | General Operate Signal | 1：enable 0：disable
| 6120 |  | PRT_Fan |  | Trip_Fan_Circuit | 1：enable 0：disable
| 6121 |  | Alm_U_DC |  | Alarm_DC Voltage Abnormal | 1：enable 0：disable
| 6122 |  | Sig_Bat_FullyDisChrgd |  | Signal_BMS Fully Charged | 1：enable 0：disable
| 6123 |  | Sig_Bat_FullyChrgd |  | Signal_BMS Fully Discharged | 1：enable 0：disable
| 6124 |  | BMS_DisChg_GateBlock |  | BMS Discharge Gate Block | 1：enable 0：disable
| 6125 |  | BMS_Chg_GateBlock |  | BMS Charge Gate Block | 1：enable 0：disable
| 6126 |  | OpTest_Start |  | IGBT open_loop test start | 1：enable 0：disable
| 6127 |  | PRT_OpTest |  | IGBT open_loop test abnormal | 1：enable 0：disable
| 6128 |  | Sig_Conv_Stopped_BMS |  | PCS stopped by BMS | 1：enable 0：disable
| 6129 |  | Mul_Protections |  | Frequent faults occurred in a short period of time. | 1：enable 0：disable
| 6130 |  | WK_RECV_Err_out_YX |  | Workstation Receive Error Output_YX | 1：enable 0：disable
| 6131 |  | WK_CTRL_first_YX |  | Workstation Control First Command_YX | 1：enable 0：disable
| 6132 |  | Backup3 |  | spare | 1：enable 0：disable
| 6133 |  | Backup4 |  | spare | 1：enable 0：disable
| 6134 |  | Backup5 |  | spare | 1：enable 0：disable
| 6135 |  | Backup6 |  | spare | 1：enable 0：disable
| 6136 |  | Backup7 |  | spare | 1：enable 0：disable
| 6137 |  | Backup8 |  | spare | 1：enable 0：disable
| 6138 |  | Backup9 |  | spare | 1：enable 0：disable
| 6139 |  | Backup10 |  | spare | 1：enable 0：disable
| 6140 |  | Op_Overall_SL |  | Overall Operation Signal_Link | 1：enable 0：disable
| 6141 |  | START_FAIL |  | Startup Failure Alarm | 1：enable 0：disable
| 6142 |  | Alm_Comm_MASL |  | Master Link Communication Alarm | 1：enable 0：disable
| 6143 |  | BH4 |  | spare | 1：enable 0：disable
| 6144 |  | BH5 |  | spare | 1：enable 0：disable
| 6145 |  | BH6 |  | spare | 1：enable 0：disable
| 6146 |  | BH7 |  | spare | 1：enable 0：disable
| 6147 |  | Sig_Stop_Total_Conv |  | Total Converter Stop Signal | 1：enable 0：disable
| 6148 |  | Sig_Standby_Total_Conv |  | Total Converter Standby Signal | 1：enable 0：disable
| 6149 |  | Sig_Online_Status_Total_Conv |  | Total Converter Online Status Signal | 1：enable 0：disable
| 6150 |  | P_Zero_GB_Total |  | Total Grid Bus Zero Active Power | 1：enable 0：disable
| 6151 |  | Grid_Off_MODE_Total |  | Total Grid Disconnection Mode | 1：enable 0：disable
| 6152 |  | Sig_Ready_BlackStart_Total_Conv |  | Total Converter Black Start Ready Signal | 1：enable 0：disable
classgrp_name="Metering" FunctionCode:04H Read only | 1 | INT | U_Bat | 电池电压 | Battery Voltage | -3276.7~+3276.7 | 0.1 | V
| 2 | INT | U_Bus_DC | 直流母线电压 | DC Busbar Voltage | -3276.7~+3276.7 | 0.1 | V
| 3 | INT | I_DC | 直流电流 | DC Current | -3276.7~+3276.7 | 0.1 | A
| 4 | INT | P_DC | 直流功率 | DC Power | -3276.7~+3276.7 | 0.1 | kW
| 5 | INT | Uab_Sys | 电网AB线电压 | Grid Uab | -3276.7~+3276.7 | 0.1 | V
| 6 | INT | Ubc_Sys | 电网BC线电压 | Grid Ubc | -3276.7~+3276.7 | 0.1 | V
| 7 | INT | Uca_Sys | 电网CA线电压 | Grid Uca | -3276.7~+3276.7 | 0.1 | V
| 8 | INT | Ua_Conv | A相电压 | Converter Ua | -3276.7~+3276.7 | 0.1 | V
| 9 | INT | Ub_Conv | B相电压 | Converter Ub | -3276.7~+3276.7 | 0.1 | V
| 10 | INT | Uc_Conv | C相电压 | Converter Uc | -3276.7~+3276.7 | 0.1 | V
| 11 | INT | Ia_Conv | A相电流 | Converter Ia | -3276.7~+3276.7 | 0.1 | A
| 12 | INT | Ib_Conv | B相电流 | Converter Ib | -3276.7~+3276.7 | 0.1 | A
| 13 | INT | Ic_Conv | C相电流 | Converter Ic | -3276.7~+3276.7 | 0.1 | A
| 14 | INT | f | 系统频率 | System Frequency | -327.67~+327.67 | 0.01 | Hz
| 15 | INT | P_Conv | 交流有功功率 | Converter AC Active Power | -3276.7~+3276.7 | 0.1 | kW
| 16 | INT | Q_Conv | 交流无功功率 | Converter AC Reactive Power | -3276.7~+3276.7 | 0.1 | kVar
| 17 | INT | PF_Conv | 功率因数 | Converter Power Factor | -327.67~+327.67 | 0.01
| 18 | INT | K_Conversion_Conv | 转换效率 | Conversion Efficiency | -327.67~+327.67 | 0.01 | %
| 19 | INT | T_Max_Module |  | Maximum Temperature_Submodule | -3276.7~+3276.7 | 0.1 | ℃
| 20 | INT | T_ModuleA1 |  | Temperature_Submodule Phase A1 sampling (Not Used) | -3276.7~+3276.7 | 0.1 | ℃
| 21 | INT | T_ModuleA2 |  | Temperature_Submodule Phase A2 sampling (Not Used) | -3276.7~+3276.7 | 0.1 | ℃
| 22 | INT | T_ModuleB1 |  | Temperature_Submodule Phase B1 sampling (Not Used) | -3276.7~+3276.7 | 0.1 | ℃
| 23 | INT | T_ModuleB2 |  | Temperature_Submodule Phase B2 sampling (Not Used) | -3276.7~+3276.7 | 0.1 | ℃
| 24 | INT | T_ModuleC1 |  | Temperature_Submodule Phase C1 sampling (Not Used) | -3276.7~+3276.7 | 0.1 | ℃
| 25 | INT | T_ModuleC2 |  | Temperature_Submodule Phase C2 sampling (Not Used) | -3276.7~+3276.7 | 0.1 | ℃
| 26 | INT | NTC_TEMP |  | Maximum Temperature_Submodule_NTC | -3276.7~+3276.7 | 0.1 | ℃
| 27 | INT | TA_NTC |  | Temperature_Submodule Phase A sampling_NTC | -3276.7~+3276.7 | 0.01 | ℃
| 28 | INT | TB_NTC |  | Temperature_Submodule Phase B sampling_NTC | -3276.7~+3276.7 | 0.01 | ℃
| 29 | INT | TC_NTC |  | Temperature_Submodule Phase C sampling_NTC | -3276.7~+3276.7 | 0.01 | ℃
| 30 | INT | U2_Conv | 变流器负序电压 | Converter Negative Voltage | -3276.7~+3276.7 | 0.1 | V
| 31 | INT | I2_Conv | 变流器负序电流 | Converter Negative Current | -3276.7~+3276.7 | 0.1 | A
| 32 | INT | U_NP | 中性点对直流负极电压 | Half Udc | -3276.7~+3276.7 | 0.1 | A
| 33 | INT | I_Leak_Conv |  | Leakage Current of Converter | -3276.7~+3276.7 | 0.1 | A
| 34 | U | Energy_Chrgd_Total | 总充电量 | Charged Energy Today | 0~65535 | 1 | kWh
| 35 | U | Energy_Dischrgd_Total | 总放电量 | Discharged Energy Today | 0~65535 | 1 | kWh
| 36 | U | Energy_Chrgd_Today | 日充电量 | Charged Energy Today | 0~65535 | 1 | kWh
| 37 | U | Energy_Dischrgd_Today | 日放电量 | Discharged Energy Today | 0~65535 | 1 | kWh
| 38 | INT | Hour_Chrg_Total | 总充电小时数 | Total Charged Hours | -3276.7~+3276.7 | 0.1 | h
| 39 | INT | Hour_Dischrg_Total | 总放电小时数 | Total Discharged Hours | -3276.7~+3276.7 | 0.1 | h
| 40 | INT | P_Setpoint_Conv | 变流器有功功率指令 | Converter Active Power Setpoint | -3276.7~+3276.7 | 0.1 | kW
| 41 | INT | Q_Setpoint_Conv | 变流器无功功率指令 | Converter Reactive Power Setpoint | -3276.7~+3276.7 | 0.1 | kVar
| 42 | INT | PF_Setpoint_Conv | 变流器功率因数指令 | Converter Power Factor Setpoint | -327.67~+327.67 | 0.01
| 43 | INT | N_Watchdog_SCADA | 后台看门狗计数 | Watchdog Counting | -32767~+32767 | 1
| 44 | INT | P_Setpoint_CCU | CCU有功功率指令 | PMS Active Power Setpoint | -3276.7~+3276.7 | 0.1 | kW
| 45 | INT | Q_Setpoint_CCU | CCU无功功率指令 | PMS Reactive Power Setpoint | -3276.7~+3276.7 | 0.1 | kVar
| 46 | INT | U_Bat_BMS | BMS电池总电压 | BMS Battery Voltage | -32767~+32767 | 1 | V
| 47 | INT | I_Bat_BMS | BMS电池组电流 | BMS Battery Current | -32767~+32767 | 1 | A
| 48 | INT | SOC_Bat_BMS | BMS电池SOC | BMS Battery SOC | -3276.7~+3276.7 | 0.1 | %
| 49 | INT | BMS_Chrg_Max_I | BMS最大充电电流 | BMS Maximum Charging Current | -3276.7~+3276.7 | 0.1 | A
| 50 | INT | BMS_Dischrg_Max_I | BMS最大放电电流 | BMS Maximum Discharging Current | -3276.7~+3276.7 | 0.1 | A
| 51 | INT | PCS_Chrg_MaxP | PCS最大充电功率 | BMS Maximum Charging Power | -3276.7~+3276.7 | 0.1 | kW
| 52 | INT | PCS_DisChrg_MaxP | PCS最大放电功率 | BMS Maximum Discharging Power | -3276.7~+3276.7 | 0.1 | kW
| 53 | U | Energy_Chrgd_Total_L |  | Total Charged Energy Low Byte_Conv | 0~65535 | 1
| 54 | U | Energy_Chrgd_Total_H |  | Total Charged Energy High Byte_Conv | 0~65535 | 1
| 55 | U | Energy_Dischrgd_Total_L |  | Total Discharged Energy Low Byte_Conv | 0~65535 | 1
| 56 | U | Energy_Dischrgd_Total_H |  | Total Discharged Energy High Byte_Conv | 0~65535 | 1
| 57 | INT | Ica_Conv | A相电容电流 | A_Capacitive current | -3276.7~+3276.7 | 0.1 | A
| 58 | INT | Icb_Conv | B相电容电流 | B_Capacitive current | -3276.7~+3276.7 | 0.1 | A
| 59 | INT | Icc_Conv | C相电容电流 | C_Capacitive current | -3276.7~+3276.7 | 0.1 | A
| 60 | INT | Fan_speed_pu | 风机风速出口值 | Fan_speed | -3276.7~+3276.7 | 0.001 | pu
| 61 | INT | NR8191 Max_Temper |  | NR8191 Board Maximum Temperature | -3276.7~+3276.7 | 0.01 | ℃
| 62 | INT | NR8191_Real_Temper |  | NR8191 Board Real-time Temperature | -3276.7~+3276.7 | 0.01 | ℃
| 63 | INT | P_Conv_Total |  | Total Converter Active Power | -3276.7~+3276.7 | 0.1 | kW
| 64 | INT | REACTIVE_Q_Total |  | Total Reactive Power | -3276.7~+3276.7 | 0.1 | kVar
| 65 | INT | WK_PREF_ORDER_YC |  | Working Preferential Control Order | -3276.7~+3276.7 | 0.001
| 66 | INT | YC4 |  | spare | -3276.7~+3276.7 | 0.001
| 67 | INT | YC5 |  | spare | -3276.7~+3276.7 | 0.001
classgrp_name="Control" FunctionCode:05H Remote control,write only | 1 |  | TrigDFR_Rmt | 遥控开关机 | Trigger Digital Fault Record Manual | FF00:close 0000:open
| 2 |  | YK_STOP/START |  | Tele-Control_Stop/Start | FF00:close 0000:open
| 3 |  | YK_STBANDBY | 遥控一键启机 | Tele-Control_Standby | FF00:close 0000:open
| 4 |  | YK_OneKeyStart | 遥控待机 | Tele-Control_One Key Start | FF00:close 0000:open
| 5 |  | YK_DCK | 遥控直流断路器 | Tele-Control_DC CB | FF00:close 0000:open
classgrp_name="Regulation" PresetSingleRegisters:06H Remote control,write only | 60001 | INT | YT_P | 遥调有功 | Tele-Regulation_Active Power | -32767~+32767 | 1 | kW
| 60002 | INT | YT_Q | 遥调无功 | Tele-Regulation_Reactive Power | -32767~+32767 | 1 | kVar
| 60003 | INT | YT_FACTOR | 遥调功率因数 | Tele-Regulation_Power Factor | -32767~+32767 | 0.01
| 60004 | INT | YT_WhDog | 遥调看门狗计数 | Tele-Regulation_Watchdog Counting | 0~32767 | 1